[image: image1.jpg]} L Ontario




Drinking-Water Systems Regulation O. Reg. 170/03


ANNUAL REPORT
	Drinking-Water System Number: 
	260060762

	Drinking-Water System Name:
	Sunny Cove Camp Well Supply

	Drinking-Water System Owner:
	Town of Fort Frances

	Drinking-Water System Category:
	Small Municipal Non-Residential System

	Period being reported:
	May 16, 2017 to October 06, 2017


Note:

The Town of Fort Frances became the owner of Sunny Cove Camp November 01, 2009.
	Complete if your Category is Large Municipal Residential or Small Municipal Residential

Does your Drinking-Water System serve more than 10,000 people?   Yes [  ]  No [  ]

Is your annual report available to the public at no charge on a web site on the Internet? 

Yes [  ]
  No [  ]
Location where Summary Report required under O. Reg. 170/03 Schedule 22 will be available for inspection. 


	Complete for all other Categories.

Number of Designated Facilities served:

Did you provide a copy of your annual report to all Designated Facilities you serve? 

Yes [ x ]  No [  ]

Number of Interested Authorities you report to:

Did you provide a copy of your annual report to all Interested Authorities you report to for each Designated Facility? 

Yes [ x ]    No [  ]




	Note: For the following tables below, additional rows or columns may be added or an appendix may be attached to the report


List all Drinking-Water Systems (if any), which receive all of their drinking water from your system:

	Drinking Water System Name
	Drinking Water System Number

	None
	


Did you provide a copy of your annual report to all Drinking-Water System owners that are connected to you and to whom you provide all of its drinking water? 

Yes [  ] No [  ] N/A [ x ]

Indicate how you notified system users that your annual report is available, and is free of charge. 
[ x ] Public access/notice via the web  

 

[ x ] Public access/notice via Government Office

[  ] Public access/notice via a newspaper 
 

[ x ] Public access/notice via Public Request

[  ] Public access/notice via a Public Library     

[  ] Public access/notice via other method _______________________________________

Describe your Drinking-Water System

LOCATION:

- Sunny Cove Camp is located approximately 12 km. east of Fort Frances on the north side of Highway 11.

- A secure well pump house houses the well and treatment equipment.

SOURCE:

- One (1) drilled well with flow restrictor (7 USGPM or 0.44L/s)

TREATMENT (Primary Disinfection):

- Iron removal and softener through two (2) R-CAN Sanitizers (71 Litres or 2.5 cu. ft)

- Filtration - dual cartridge with 5μm filters

- Primary disinfection provided by chlorination – dual chlorine-metering pumps (one duty, one standby) and double-wall chemical solution tank

- Treated water passes through two (2) chlorine contact tanks, 300 L (80 USGal) per tank to ensure chlorine contact time (CT) is met.

- System is pressurized by pressure tank operating at pressures between 40 – 60 psi. Once below 40 psi the well pump and the duty chlorine-metering pump will come on

OTHER COMPONENTS:

- Backwash water for the R-CAN Sanitizer is directed to a fabric wrapped perforated pipe buried in crushed rock located just behind the pump house.

List all water treatment chemicals used over this reporting period

	Sodium hypochlorite (5-20%) for primary treatment

Crystal-Right CR200 – silica crystal media for water softening, iron and manganese removal

Potassium Chloride – brine mixture




Were any significant expenses incurred to? 

[    ]  Install required equipment

[    ]  Repair required equipment

[    ]  Replace required equipment

      Please provide a brief description and a breakdown of monetary expenses incurred

No Upgrades to Water System in 2017.
Provide details on the notices submitted in accordance with subsection 18(1) of the Safe Drinking-Water Act or section 16-4 of Schedule 16 of O.Reg.170/03 and reported to Spills Action Centre  

	Incident Date
	Parameter
	Result
	Unit of Measure
	Corrective Action
	Corrective Action Date

	None to report in 2017


Microbiological testing done under the Schedule 10, 11 or 12 of Regulation 170/03, during this reporting period.
	
	Number of Samples 
	Range of E.Coli Or Fecal

Results 

(min #)-(max #)


	Range of Total Coliform Results

(min #)-(max #)


	Number 

of HPC Samples 
	Range of HPC Results

(min #)-(max #)

	Raw
	7
	E.C.: 0 - 0
	0 - 0
	N/A
	N/A

	Treated
	N/A
	N/A
	N/A
	N/A
	N/A

	Distribution
	7
	0
	0
	7
	0 - 0


Operational testing done under Schedule 7, 8 or 9 of Regulation 170/03 during the period covered by this Annual Report.

	
	Number of Grab Samples
	Range of Results

(min #)-(max #)



	Turbidity
	N/A
	

	Chlorine - Treatment
	74
	0.72 to 2.20

	Chlorine - Distribution
	74
	0.13 to 2.20

	Fluoride (If the DWS provides fluoridation)
	N/A
	


	NOTE: Record the unit of measure if it is not milligrams per litre.


Summary of additional testing and sampling carried out in accordance with the requirement of an approval, order or other legal instrument.
	Date of legal instrument issued
	Parameter 
	Date Sampled
	Result
	Unit of Measure

	None
	
	
	
	


Summary of Inorganic parameters tested during this reporting period or the most recent sample results

	Parameter
	Sample Date 
	Result Value
	Unit of Measure
	Exceedance

	Antimony
	May 13, 2014
	<0.60
	µg/L
	No

	Arsenic
	May 13, 2014
	<1.0
	µg/L
	No

	Barium
	May 13, 2014
	<10
	µg/L
	No

	Boron
	May 13, 2014
	71
	µg/L
	No

	Cadmium
	May 13, 2014
	<0.10
	µg/L
	No

	Chromium
	May 13, 2014
	<1.0
	µg/L
	No

	*Lead
	August 09, 2017
	<1.0
	µg/L
	No

	Mercury
	May 13, 2014
	<0.10
	µg/L
	No

	Selenium
	May 13, 2014
	<5.0
	µg/L
	No

	Sodium
	May 13, 2014
	9.05
	mg/L
	No

	Uranium
	May 13, 2014
	<5.0
	µg/L
	No

	Fluoride
	May 13, 2014
	0.177
	mg/L
	No

	Nitrite
	August 09, 2017
	<0.010
	mg/L
	No

	Nitrate
	August 09, 2017
	<0.020
	mg/L
	No


     *only for drinking water systems testing under Schedule 15.2; this includes large municipal non-residential systems, small municipal non-residential systems, non-municipal seasonal residential systems, large non-municipal non-residential systems, and small non-municipal non-residential systems

Summary of lead testing under Schedule 15.1 during this reporting period 

(applicable to the following drinking water systems; large municipal residential systems, small

 municipal residential systems, and non-municipal year-round residential systems) 

	Location Type
	Number of Samples
	Range of Lead Results 

(min#) – (max #)
	Number of Exceedances

	Plumbing 
	N/A
	
	

	Distribution
	N/A
	
	


Summary of Organic parameters sampled during this reporting period or the most recent sample results

	Parameter
	Sample Date 
	Result Value
	Unit of Measure
	Exceedance

	Alachlor
	May 13, 2014
	<0.10
	µg/L
	No

	Aldicarb
	May 13, 2014
	<1.0
	µg/L
	No

	Aldrin + Dieldrin
	May 13, 2014
	<0.040
	µg/L
	No

	Atrazine + N-dealkylated metobolites
	May 13, 2014
	<0.20
	µg/L
	No

	Azinphos-methyl
	May 13, 2014
	<0.10
	µg/L
	No

	Bendiocarb
	May 13, 2014
	<0.20
	µg/L
	No

	Benzene
	May 13, 2014
	<0.50
	µg/L
	No

	Benzo(a)pyrene
	May 13, 2014
	<0.010
	µg/L
	No

	Bromoxynil
	May 13, 2014
	<0.20
	µg/L
	No

	Carbaryl
	May 13, 2014
	<0.20
	µg/L
	No

	Carbofuran
	May 13, 2014
	<0.20
	µg/L
	No

	Carbon Tetrachloride
	May 13, 2014
	<0.50
	µg/L
	No

	Chlordane (Total)
	May 13, 2014
	<0.30
	µg/L
	No

	Chlorpyrifos
	May 13, 2014
	<0.10
	µg/L
	No

	Cyanazine
	May 13, 2014
	<0.10
	µg/L
	No

	Diazinon
	May 13, 2014
	<0.10
	µg/L
	No

	Dicamba
	May 13, 2014
	<0.20
	µg/L
	No

	1,2-Dichlorobenzene
	May 13, 2014
	<0.50
	µg/L
	No

	1,4-Dichlorobenzene
	May 13, 2014
	<0.50
	µg/L
	No

	Dichlorodiphenyltrichloroethane (DDT) + metabolites
	May 13, 2014
	<0.40
	µg/L
	No

	1,2-Dichloroethane
	May 13, 2014
	<0.50
	µg/L
	No

	1,1-Dichloroethylene

(vinylidene chloride)
	May 13, 2014
	<0.50
	µg/L
	No

	Dichloromethane
	May 13, 2014
	<5.0
	µg/L
	No

	2-4 Dichlorophenol
	May 13, 2014
	<0.30
	µg/L
	No

	2,4-Dichlorophenoxy acetic acid (2,4-D)
	May 13, 2014
	<0.20
	µg/L
	No

	Diclofop-methyl
	May 13, 2014
	<0.20
	µg/L
	No

	Dimethoate
	May 13, 2014
	<0.10
	µg/L
	No

	Dinoseb
	May 13, 2014
	<0.20
	µg/L
	No

	Diquat
	May 13, 2014
	<1.0
	µg/L
	No

	Diuron
	May 13, 2014
	<1.0
	µg/L
	No

	Glyphosate
	May 13, 2014
	<5.0
	µg/L
	No

	Heptachlor + Heptachlor Epoxide
	May 13, 2014
	<0.20
	µg/L
	No

	Lindane (Total)
	May 13, 2014
	<0.10
	µg/L
	No

	Malathion
	May 13, 2014
	<0.10
	µg/L
	No

	Methoxychlor
	May 13, 2014
	<0.10
	µg/L
	No

	Metolachlor
	May 13, 2014
	<0.10
	µg/L
	No

	Metribuzin
	May 13, 2014
	<0.10
	µg/L
	No

	Monochlorobenzene
	May 13, 2014
	<0.50
	µg/L
	No

	Paraquat
	May 13, 2014
	<1.0
	µg/L
	No

	Parathion
	May 13, 2014
	<0.10
	µg/L
	No

	Pentachlorophenol
	May 13, 2014
	<0.50
	µg/L
	No

	Phorate
	May 13, 2014
	<0.10
	µg/L
	No

	Picloram
	May 13, 2014
	<0.20
	µg/L
	No

	Polychlorinated Biphenyls(PCB)
	May 13, 2014
	<0.035
	µg/L
	No

	Prometryne
	May 13, 2014
	<0.10
	µg/L
	No

	Simazine
	May 13, 2014
	<0.10
	µg/L
	No

	THM 

(NOTE: show latest annual average)
	
	
	
	

	Temephos
	May 13, 2014
	<0.10
	µg/L
	No

	Terbufos
	May 13, 2014
	<0.20
	µg/L
	No

	Tetrachloroethylene
	May 13, 2014
	<0.50
	µg/L
	No

	2,3,4,6-Tetrachlorophenol
	May 13, 2014
	<0.50
	µg/L
	No

	Triallate
	May 13, 2014
	<0.10
	µg/L
	No

	Trichloroethylene
	May 13, 2014
	<0.50
	µg/L
	No

	2,4,6-Trichlorophenol
	May 13, 2014
	<0.50
	µg/L
	No

	2,4,5-Trichlorophenoxy acetic acid (2,4,5-T)
	May 13, 2014
	<0.20
	µg/L
	No

	Trifluralin
	May 13, 2014
	<0.10
	µg/L
	No

	Vinyl Chloride
	May 13, 2014
	<0.20
	µg/L
	No


List any Inorganic or Organic parameter(s) that exceeded half the standard prescribed in Schedule 2 of Ontario Drinking Water Quality Standards.

	Parameter
	Result Value
	Unit of Measure
	Date of Sample

	
	
	
	








1





1





NOTE: For continuous monitors use 8760 as the number of samples.








	Drinking Water Systems Regulations

(PIBS 4435e01) February 2008
	Page 1 of 5





